## INPUTS (hidden)
Air Cooled Chiller
Program Level Inputs
Description | Code | Value
Min Path-A IPLV for <150 | ac_LT150 MinIPLVA | 13.7
Min Path-A IPLV for >=150 | ac_GT150 MinIPLVA | 14
Path A Prog Qual EER | ac_EERQualA | 10.5208 | Min qualifier | Air Cooled Chiller Rebate: Refer to Tab "AirC Calculations"
Path A Min EER | ac_EERMinA | 10.1 | Base | Water Cooled Centrifugal Rebate: Refer to Tab "WaterC Centrif Calculations"
Min Path-B IPLV for <150 | ac_LT150 MinIPLVB | 15.8 |  | Water Cooled Positive Displacement Rebate: Refer to Tab "WaterC Pos Disp Calc"
Min Path-B IPLV for >=150 | ac_GT150 MinIPLVB | 16.1
Path B Prog Qual EER | ac_EERQualB | 10.1042 | Min qualifier
Path B Min EER | ac_EERMinB | 9.7 | Base
kW to Summer kW Factor | ac_SkWFact | 100%
kW to Winter kW Factor | ac_WkWFact | 21.5%
KW to kWh | ac_kWhFact | 4152
Incentive $/kW | ac_Incent per kW | 145
Base Energy Factor | ac_BEF | 105%
* Note: 4% incremental qualification formula should be included here, same as water cooled chiller; as part of the input values
Water Cooled Centrifugal Chiller |  |  |  | Water Cooled Positive Chiller
#DIV/0!
Program Level Inputs |  |  |  | Program Level Inputs
Description | Code | Value |  | Description | Code | Value
Min Path-A IPLV for <150 | wcc_LT150 MinIPLVA | 0.55 |  | Min Path-A IPLV for <75 | wcp_LT75 MinIPLVA | 0.6
Min Path-A IPLV for <=150 to <300 | wcc_151to300 MinIPLVA | 0.55 |  | Min Path-A IPLV for <=75 to< 150 | wcp_76to150 MinIPLVA | 0.56
Min Path-A IPLV for <=300 to <400 | wcc_301to400 MinIPLVA | 0.52 |  | Min Path-A IPLV for <=150 to <300 | wcp_151to300 MinIPLVA | 0.54
Min Path-A IPLV for <=400 to <600 | wcc_401to600 MinIPLVA | 0.5 |  | Min Path-A IPLV for <=300 to <600 | wcp_301to600 MinIPLVA | 0.52
Min Path-A IPLV for >=600 | wcc_GT600 MinIPLVA | 0.5 |  | Min Path-A IPLV for >=600 | wcp_GT600 MinIPLVA | 0.5 |  | WCC | WCP
Path A Program Qual EER <150 | wcc_EERQualA-LT150 | 20.4896 | calc | Path A Prog Qual EER<75 | wcp_EERQualA_LT75 | 16.6667 | calc | 20.49 | 16.67
Path A Min EER <150 | wcc_EERMinA-LT150 | 19.67 | ASHRAE | Path A Min EER <75 | wcp_EERMinA_LT75 | 16 | ASHRAE | 19.67 | 16
Path A Program Qual EER <=150 to <300 | wcc_EERQualA-151to300 | 20.4896 | calc | Path A Prog Qual EER <=75 to< 150 | wcp_EERQualA_76to150 | 17.3646 | calc | 20.49 | 17.36
Path A Min EER <=150 to <300 | wcc_EERMinA-151to300 | 19.67 | ASHRAE | Path A Min EER <=75 to< 150 | wcp_EERMinA_76to150 | 16.67 | ASHRAE | 19.67 | 16.67
Path A Program Qual EER <=300 to <400 | wcc_EERQualA-301to400 | 22.3229 | calc | Path A Prog Qual EER <=150 to <300 | wcp_EERQualA_151to300 | 18.9375 | calc | 22.32 | 18.94
Path A Min EER <=300 to <400 | wcc_EERMinA-301to400 | 21.43 | ASHRAE | Path A Min EER <=150 to <300 | wcp_EERMinA_151to300 | 18.18 | ASHRAE | 21.43 | 18.18
Path A Program Qual EER <=400 to <600 | wcc_EERQualA-401to600 | 22.3229 | calc | Path A Prog Qual EER <=300 to <600 | wcp_EERQualA_301to600 | 20.4896 | calc | 22.32 | 20.49
Path A Min EER <=400 to <600 | wcc_EERMinA-401to600 | 21.43 | ASHRAE | Path A Min EER <=300 to <600 | wcp_EERMinA_301to600 | 19.67 | ASHRAE | 21.43 | 19.67
Path A Program Qual EER >=600 | wcc_EERQualA-GT600 | 22.3229 | calc | Path A Prog Qual EER >=600 | wcp_EERQualA_GT600 | 22.3229 | calc | 22.32 | 22.32
Path A Min EER >=600 | wcc_EERMinA-GT600 | 21.43 | ASHRAE | Path A Min EER >=600 | wcp_EERMinA_GT600 | 21.43 | ASHRAE | 21.43 | 21.43
Min Path B IPLV for <150 | wcc_LT150 MinIPLVB | 0.44 |  | Min Path B IPLV for <75 | wcp_LT75 MinIPLVB | 0.5
Min Path B IPLV for <=150 to <300 | wcc_151to300 MinIPLVB | 0.4 |  | Min Path B IPLV for <=75 to <150 | wcp_76to150 MinIPLVB | 0.49
Min Path B IPLV for <=300 to <400 | wcc_301to400 MinIPLVB | 0.39 |  | Min Path B IPLV for <=150 to <300 | wcp_151to300MinIPLVB | 0.44
Min Path B IPLV for <=400 to <600 | wcc_401to600 MinIPLVB | 0.38 |  | Min Path B IPLV for <=300 to <600 | wcp_301to600 MinIPLVB | 0.41
Min Path B IPLV for >=600 | wcc_GT600 MinIPLVB | 0.38 |  | Min Path B IPLV for >=600 | wcp_GT600 MinIPLVB | 0.38 |  | WCC | WCP
Path B Program Qual EER<150 | wcc_EERQualB_LT150 | 17.9896 | calc | Path B Program Qual EER<75 | wcp_EERQualB_LT75 | 16.0208 | calc | 17.99 | 16.03
Path B Min EER <150 | wcc_EERMinB_LT150 | 17.27 | ASHRAE | Path B Min EER <75 | wcp_EERMinB_LT75 | 15.38 | ASHRAE | 17.27 | 15.38
Path B Program Qual EER <=150 to <300 | wcc_EERQualB_151to300 | 19.6875 | calc | Path B Program Qual EER <=75 to <150 | wcp_EERQualB_76to150 | 16.6667 | calc | 19.69 | 16.67
Path B Program Qual EER <=150 to <300 | wcc_EERMinB_151to300 | 18.9 | ASHRAE | Path B Min EER<=75 to <150 | wcp_EERMinB_76to150 | 16 | ASHRAE | 18.9 | 16
Path B Program Qual EER <=300 to <400 | wcc_EERQualB_301to400 | 21.0104 | calc | Path B Program Qual EER <=150 to <300 | wcp_EERQualB_151to300 | 18.3854 | calc | 21.01 | 18.38
Path B Min EER <=300 to <400 | wcc_EERMinB_301to400 | 20.17 | ASHRAE | Path B Min EER <=150 to <300 | wcp_EERMinB_151to300 | 17.65 | ASHRAE | 20.17 | 17.65
Path B Program Qual EER <=400 to <600 | wcc_EERQualB_401to600 | 21.3646 | calc | Path B Program Qual EER <=300 to <600 | wcp_EERQualB_301to600 | 20 | calc | 21.37 | 20
Path B Min EER <=400 to <600 | wcc_EERMinB_401to600 | 20.51 | ASHRAE | Path B Min EER <=300 to <600 | wcp_EERMinB_301to600 | 19.2 | ASHRAE | 20.51 | 19.2
Path B Program Qual EER >=600 | wcc_EERQualB_GT600 | 21.3646 | calc | Path B Program Qual EER >=600 | wcp_EERQualB_GT600 | 21.3646 | calc | 21.37 | 21.37
Path B Min EER >=600 | wcc_EERMinB_GT600 | 20.51 | ASHRAE | Path B Min EER >=600 | wcp_EERMinB_GT600 | 20.51 | ASHRAE | 20.51 | 20.51
kW to Summer kW Factor | wc_SkWFact | 100%
kW to Winter kW Factor | wc_WkWFact | 21.5%
KW to kWh | wc_kWhFact | 4152
Incentive $/kW | wc_Incent per kW | 145
Base Energy Factor | wc_BEF | 100%
General Min kW per Ton Reduction | GenMinkWperTonPerc | 4%
*Note: We should be able to enter EER or Kw/Ton as part of the input values

## AirC Calculations
Air Cooled Chillers
Official Path | PATH A
150 or Above | PATH A
Less than 150 | OTHER
Path A SkW | 10.5865 |  |  | Fundamental base equation: |  |  | Basic Flow
Path A WkW | 2.2761 |  |  | kWat the meter = Tonsnew x (12/EERbase – 12/EERnew) |  |  | 1. Determine Path A or Path B for given size of equipment
Path A kWh | 43955.0306 | [5 empty] | 2. Determine if EER meets minimum based on size and path
Path A Icentive | 1535.0384 |  |  | Qualification criteria calculations applied prior to calculation of Indicators |  |  | 3. Calculate kW at the meter
4. Calculate Program Indicators
Path B SkW | 18.3717 |  |  | Transformation equations to SkW, WkW, GWh, Incentive:
Path B WkW | 3.9499 |  |  | Indicator = Factor per kW x kWon premise
Path B kWh | 76279.3487
Path B Icentive | 2663.8983
Air Cooled Chiller Calculation
Required Inputs: Chiller AC Tonage, EER, IPLV
PATH A
Job Specific Inputs | Air Cooled | Air Cooled
Description | Code | Value
Program | Program | Chillers
Nameplate AC Type | Type | Air Cooled
Nameplate AC Tonage | ac_ACTons | 158.9
Nameplate Efficiency (EER or kW/ton) |  | 10.7
Nameplate EER | ac_EERN | 10.7
Nameplate IPLV (EER or kW/ton) |  | 14.8
Nameplate IPLV | ac_IPLVN | 14.8
Number of like units installed |  | 1
Results |  |  | If multiple units |  | Check 1 | Does it pass IPLV and then the path
Summer kW |  | 10.5865 | 10.5865 |  | Check 2 | Does it meet minimum EER
Winter kW |  | 2.2761 | 2.2761
kWh |  | 43955.0306 | 43955.0306
Incentive |  | 1535.0384 | 1535.0384
DNQ = DOES NOT QUALIFY
For additional support:
Business HVAC Program Support: |  | Mike.Catarzi@fpl.com
Gary.R.Reynolds@fpl.com
Busines HVAC Technical Support: |  | Chi.Lui@fpl.com
Abel.Alonso@fpl.com

## WaterC Centrif Calculations
Water Cooled Centrifugal |  |  |  | Fundamental base equation: |  |  |  | Basic Flow
WC Centrigugal Path | wcc_Path | PATH A |  | kWat the meter = Tonsnew x (12/EERbase – 12/EERnew) |  |  |  | 1. Determine Path A or Path B for given size of equipment
Path LT151 | wcc_PathLT150 | PATH A | [5 empty] | 2. Determine if EER meets minimum based on size and path
Path 150 to 300 Above | wcc_Path151to300 | OTHER |  | Qualification criteria calculations applied prior to calculation of Indicators |  |  |  | 3. Calculate kW at the meter
Path 300 to 400 Above | wcc_PathLT301to400 | OTHER | [5 empty] | 4. Calculate Program Indicators
Path 400 to 600 Above | wcc_PathLT401to600 | OTHER |  | Transformation equations to SkW, WkW, GWh, Incentive:
Path GT 600 | wcc_PathGT600 | OTHER |  | Indicator = Factorper kW x kWon premise
Path A SkW | wcc_PathA_SkW | 3.8767 |  | Path A WkW | wcc_PathA_WkW | 0.83349 | Path A kWh | wcc_PathA_kWh | 16096.0281 | Path A Icentive | wcc_PathA_Inc | 562.1204
Path A SkW LT150 | wcc_PA_ SkWLT150 | 3.8767 |  | Path A WkW LT151 | wcc_PA_ WkWLT150 | 0.83349 | Path A kWh LT151 | wcc_PA_ kWhLT150 | 16096.0281 | Path A Inc LT151 | wcc_PA_ IncLT150 | 562.1204
Path A SkW 150 to 300 | wcc_PA_ SkW151to300 | OTHER |  | Path A WkW 150 to 300 | wcc_PA_ WkW151to300 | OTHER | Path A kWh 150 to 300 | wcc_PA_ kWh151to300 | OTHER | Path A Inc 150 to 300 | wcc_PA_ Inc151to300 | OTHER
Path A SkW 300 to 400 | wcc_PA_ SkW301to400 | OTHER |  | Path A WkW 300 to 400 | wcc_PA_ WkW301to400 | OTHER | Path A kWh 300 to 400 | wcc_PA_ kWh301to400 | OTHER | Path A Inc 300 to 400 | wcc_PA_ Inc301to400 | OTHER
Path A SkW 400 to 600 | wcc_PA_ SkW401to600 | OTHER |  | Path A WkW 400 to 600 | wcc_PA_ WkW401to600 | OTHER | Path A kWh 400 to 600 | wcc_PA_ kWh401to600 | OTHER | Path A Inc 400 to 600 | wcc_PA_ Inc401to600 | OTHER
Path A SkW GT 600 | wcc_PA_ SkWGT600 | OTHER |  | Path A WkW GT 600 | wcc_PA_ WkWGT600 | OTHER | Path A kWh GT 600 | wcc_PA_ kWhGT600 | OTHER | Path A Inc GT 600 | wcc_PA_ IncGT600 | OTHER
Path B SkW | wcc_PB_SkW | 8.9635 |  | Path B WkW | wcc_PB_WkW | 1.9272 | Path B kWh | wcc_PB_kWh | 37216.5373 | Path B Icentive | wcc_PB_Inc | 1299.7105
Path B SkW LT150 | wcc_PB_ SkWLT150 | 8.9635 |  | Path B WkW LT151 | wcc_PB_ WkWLT150 | 1.9272 | Path B kWh LT151 | wcc_PB_ kWhLT150 | 37216.5373 | Path B Inc LT151 | wcc_PB_ IncLT150 | 1299.7105
Path B SkW 150 to 300 | wcc_PB_ SkW151to300 | OTHER |  | Path B WkW 150 to 300 | wcc_PB_ WkW151to300 | OTHER | Path B kWh 150 to 300 | wcc_PB_ kWh151to300 | OTHER | Path B Inc 150 to 300 | wcc_PB_ Inc151to300 | OTHER
Path B SkW 300 to 400 | wcc_PB_ SkW301to400 | OTHER |  | Path B WkW 300 to 400 | wcc_PB_ WkW301to400 | OTHER | Path B kWh 300 to 400 | wcc_PB_ kWh301to400 | OTHER | Path B Inc 300 to 400 | wcc_PB_ Inc301to400 | OTHER
Path B SkW 400 to 600 | wcc_PB_ SkW401to600 | OTHER |  | Path B WkW 400 to 600 | wcc_PB_ WkW401to600 | OTHER | Path B kWh 400 to 600 | wcc_PB_ kWh401to600 | OTHER | Path B Inc 400 to 600 | wcc_PB_ Inc401to600 | OTHER
Path B SkW GT 600 | wcc_PB_ SkWGT600 | OTHER |  | Path B WkW GT 600 | wcc_PB_ WkWGT600 | OTHER | Path B kWh GT 600 | wcc_PB_ kWhGT600 | OTHER | Path B Inc GT 600 | wcc_PB_ IncGT600 | OTHER
Water Cooled Centrifugal Chiller Calculation
Required Inputs: Chiller AC Tonage, EER, IPLV
PATH A
Job Specific Inputs |  | Water Cooled Centrifugal
Description | Variable Code | Value
Program | Program | Water Cooled
Nameplate AC Type | Type | Centrifugal
Nameplate AC Tonage | wcc_ACTons | 60
Nameplate Efficiency (EER or kW/ton) |  | 22
Nameplate EER | wcc_EERN | 22
Nameplate IPLV (EER or kW/ton) |  | 0.55
Nameplate IPLV | wcc_IPLVN | 0.55
Number of like Units Installed |  | 1
Results |  |  | If multiple units
Summer kW |  | 3.8767 | 3.8767
Winter kW |  | 0.83349 | 0.83349
kWh |  | 16096.0281 | 16096.0281
Incentive |  | 562.1204 | 562.1204
DNQ = DOES NOT QUALIFY
For additional support:
Business HVAC Program Support: |  | Mike.Catarzi@fpl.com
Gary.R.Reynolds@fpl.com
Busines HVAC Technical Support: |  | Chi.Lui@fpl.com
Abel.Alonso@fpl.com

## WaterC Pos Disp Calc
Water Cooled Positive Displacement |  |  | Fundamental base equation: |  |  |  |  | Basic Flow
WC Pos Disp Path | wcp_Path | PATH B | kWat the meter = Tonsnew x (12/EERbase – 12/EERnew) |  |  |  |  | 1. Determine Path A or Path B for given size of equipment
Path LT75 | wcp_PathLT75 | OTHER | [5 empty] | 2. Determine if EER meets minimum based on size and path
Path 75 to 150 | wcp_Path76to150 | OTHER | Qualification criteria calculations applied prior to calculation of Indicators |  |  |  |  | 3. Calculate kW at the meter
Path 150 to 300 | wcp_PathLT151to300 | PATH B | [5 empty] | 4. Calculate Program Indicators
Path 300 to 600 | wcp_PathLT301to600 | OTHER | Transformation equations to SkW, WkW, GWh, Incentive:
Path GT 600 | wcp_PathGT600 | OTHER | Indicator = Factor per kW x kWon premise
Path A Inc | wcp_PA_SkW | 8.9685 | Path A WkW | wcp_PA_WkW | 1.9282 | Path A kWh | wcp_PA_kWh | 37237.3011 | Path A Icentive | wcp_PA_Inc | 1300.4356
Path LT75 | wcp_PathLT75 | OTHER | Path A WkW LT151 | wcp_PA_ WkWLT150 | OTHER | Path A kWh LT151 | wcp_PA_ kWhLT150 | OTHER | Path A Inc LT151 | wcp_PA_ IncLT150 | OTHER
Path 75 to 150 | wcp_Path76to150 | OTHER | Path A WkW 150 to 300 | wcp_PA_ WkW151to300 | OTHER | Path A kWh 150 to 300 | wcp_PA_ kWh151to300 | OTHER | Path A Inc 150 to 300 | wcp_PA_ Inc151to300 | OTHER
Path 150 to 300 | wcp_PathLT151to300 | 8.9685 | Path A WkW 300 to 400 | wcp_PA_ WkW301to400 | 1.9282 | Path A kWh 300 to 400 | wcp_PA_ kWh301to400 | 37237.3011 | Path A Inc 300 to 400 | wcp_PA_ Inc301to400 | 1300.4356
Path 300 to 600 | wcp_PathLT301to600 | OTHER | Path A WkW 400 to 600 | wcp_PA_ WkW401to600 | OTHER | Path A kWh 400 to 600 | wcp_PA_ kWh401to600 | OTHER | Path A Inc 400 to 600 | wcp_PA_ Inc401to600 | OTHER
Path GT 600 | wcp_PathGT600 | OTHER | Path A WkW GT 600 | wcp_PA_ WkWGT600 | OTHER | Path A kWh GT 600 | wcp_PA_ kWhGT600 | OTHER | Path A Inc GT 600 | wcp_PA_ IncGT600 | OTHER
Path B Inc | wcp_PB_SkW | 13.3291 | Path B WkW | wcp_PB_WkW | 2.8658 | Path B kWh | wcp_PB_kWh | 55342.3021 | Path B Icentive | wcp_PB_Inc | 1932.7153
Path LT75 | wcp_PathLT75 | OTHER | Path B WkW LT151 | wcp_PB_ WkWLT150 | OTHER | Path B kWh LT151 | wcp_PB_ kWhLT150 | OTHER | Path B Inc LT151 | wcp_PB_ IncLT150 | OTHER
Path 75 to 150 | wcp_Path76to150 | OTHER | Path B WkW 150 to 300 | wcp_PB_ WkW151to300 | OTHER | Path B kWh 150 to 300 | wcp_PB_ kWh151to300 | OTHER | Path B Inc 150 to 300 | wcp_PB_ Inc151to300 | OTHER
Path 150 to 300 | wcp_PathLT151to300 | 13.3291 | Path B WkW 300 to 400 | wcp_PB_ WkW301to400 | 2.8658 | Path B kWh 300 to 400 | wcp_PB_ kWh301to400 | 55342.3021 | Path B Inc 300 to 400 | wcp_PB_ Inc301to400 | 1932.7153
Path 300 to 600 | wcp_PathLT301to600 | OTHER | Path B WkW 400 to 600 | wcp_PB_ WkW401to600 | OTHER | Path B kWh 400 to 600 | wcp_PB_ kWh401to600 | OTHER | Path B Inc 400 to 600 | wcp_PB_ Inc401to600 | OTHER
Path GT 600 | wcp_PathGT600 | OTHER | Path B WkW GT 600 | wcp_PB_ WkWGT600 | OTHER | Path B kWh GT 600 | wcp_PB_ kWhGT600 | OTHER | Path B Inc GT 600 | wcp_PB_ IncGT600 | OTHER
Water Cooled Positive Displacement Chiller Calculation
Required Inputs: Chiller AC Tonage, EER, IPLV
PATH B
Job Specific Inputs |  | Water Cooled Positive Displacement
Description | Variable Code | Value
Program | Program | Water Cooled
Nameplate AC Type | Type | Pos Displacement
Nameplate AC Tonage | wcp_ACTons | 220
Nameplate Efficiency (EER or kW/ton) |  | 0.6193
Nameplate EER | wcp_EERN | 19.3767
Nameplate IPLV (EER or kW/ton) |  | 0.3779
Nameplate IPLV | wcp_IPLVN | 0.3779
Number of like Units Installed |  | 1
Results |  |  | If multiple units
Summer kW |  | 13.3291 | 13.3291
Winter kW |  | 2.8658 | 2.8658
kWh |  | 55342.3021 | 55342.3021
Incentive |  | 1932.7153 | 1932.7153
DNQ = DOES NOT QUALIFY
For additional support:
Business HVAC Program Support: |  | Mike_Catarzi@fpl.com
Gary.R.Reynolds@fpl.com
Busines HVAC Technical Support: |  | Chi_Lui@fpl.com
Abel.Alonso@fpl.com