## DXAC Prog and Lookup
DX Program Level Inputs
|  | Qualifier factor - x% better than MinQual | 107% |  |  |  |  | 12.84
|  |  | EER |  |  | IEER
|  | Minimum Qualified Efficiency for less than 65 Mbtuh | 13.4 |  |  |  | Min_EER_65 |  | Fundamental base equation:
|  | Minimum Qualified Efficiency for 65 ≤ MBtuh < 135 | 11.2 |  |  | 14.8 | Min_EER_65_135 |  | kWat the meter = | (Unit Capacity Mbtuh/12 * (12/EERbase – 12/EERnew)) * BES Factor
|  | Minimum Qualified Efficiency for 135 ≤ MBtuh < 240 | 11 |  |  | 14.2 | Min_EER_135_240 |  | Unit Capacity Mbtuh/12: | Conversion Mbtuh to Ton
|  | Minimum Qualified Efficiency for 240 ≤ MBtuh < 760 | 10 |  |  | 13.2 | Min_EER_240_760 |  | 12/EERbase: | Conversion EE_SEER2_IEER to KW/Ton
|  | Minimum Qualified Efficiency for MBtuh ≥ 760 | 9.7 |  |  | 12.5 | MIN_EER_760 |  | 12/EERnew: | Conversion EE_SEER2_IEER to KW/Ton
|  | Capacity 65 Mbtuh | 65 |  |  |  | Capacity_65_Mbtuh
|  | Capacity 135 Mbtuh | 135 |  |  |  | Capacity_135_Mbtuh |  | Qualification criteria calculations applied prior to calculation of Indicators
|  | Capacity 240 Mbtuh | 240 |  |  |  | Capacity_240_Mbtuh
|  | Capacity 760 Mbtuh | 760 |  |  |  | Capacity_760_Mbtuh |  | Transformation equations to SkW, WkW, GWh, Incentive (OUTPUT):
|  | FPL Rebate $/KW ===> | 165 |  |  |  | FPL_Rebate |  | Indicator = | Factor per kW * kWon premise
|  | BES Factor | 0.889 |  |  |  | BES_Factor |  | Indicator (Summer KW Reduction) = | Summer KW Factor * Summer KW Reduction
|  | SEER2 Factor less than 65 Mbtuh | 0.97 |  |  |  | SEER2_Factor_less_than_65_Mbtuh |  | Indicator (Winter KW Reduction) = | Winter KW Factor * Summer KW Reduction
| new field | Base IEER to EER Factor more than 65 Mbtuh | 1.2995 |  |  |  | Base_IEER_to_EER_Factor_more_than_65_Mbtuh
|  | New IEER to EER Factor more than 65 Mbtuh | 1 |  |  |  | New_IEER_to_EER_Factor_more_than_65_Mbtuh |  | Indicator (KWh Reduction) = | KWh Factor * Summer KW Reduction
|  | Summer kW Factor | 1 |  |  |  | Summer_kW_Factor
|  | Winter kW Factor | 0.983 |  |  |  | Winter_kW_Factor |  | Rebate Amount:
|  | kWh Factor | 3796.3 |  |  |  | kWh_Factor |  | Rebate Amount = | Summer KW Reduction * FPL Rebate
|  | Heat Pump | Yes |  |  |  | Heat_Pump
|  |  | No | [5 empty] | Data Validation:
|  | Water Cooled Weighted Average | 0.875
|  | EFFICIENCY CONDITIONS | [6 empty] | EER | System Capacity must be >= 65Mbtuh
|  | Base Efficiency EER Qualifier | 0 |  |  |  | Base_Efficiency_EER |  | SEER2 | System Capacity must be < 65Mbtuh
|  | Base Efficiency SEER Qualifier | 14.338 | [5 empty] | IEER | Energy Efficiency Ratio
|  | Base Efficiency SEER2 Qualifier | 0 | [5 empty] | SEER | Seasonal Energy Efficiency Ratio 2
| new field | Base Efficiency IEER Qualifier | 0 | [6 empty] | Integrated Energy Efficiency Ratio
|  | Minimum Qualified Efficiency (SEER, SEER2, EER, IEER) | 13.4 |  |  |  | Calculated_Base_Efficiency
|  | Calculated New Efficiency | 17 |  |  |  | Calculated_New_Efficiency
|  | Qualification | Qualify | [5 empty] | DNQ | Do Not Qualify
Qualify
Direct Expansion Unit (DX)
|  | Type of Efficiency Rating (EER/SEER/SEER2/IEER) | SEER
|  | Heat Pump | Yes
|  | Water Cooled | No |  |  |  | On UI, we will reuse Chiller/Compressor type field with two selection as "Air Cooled" and "Water Cooled"
|  | System Capacity (Mbtuh) | 36 | 1.34 | SELECT SEER/SEER2 FOR SYSTEM CAPACITY LESS THAN 65 MBTUH
|  | Efficiency Rating (EER/SEER/SEER2/IEER) | 17 | 14.3
|  | Number of Units Installed | 3
|  | Results |  |  | If multiple units
| revised formula | KW Reduction at Meter | 0.50577 |  | 1.5173 | 0.50577
|  | Summer KW Reduction (SKW) | 0.50577 |  | 1.5173 | 0.50577
|  | Winter KW Reduction (WKW) | 0.49717 |  | 1.4915 | 0.49717
|  | kWh Reduction (KWH) | 1920.0546 |  | 5760.1637 | 1920.0546
|  | Incentive | 83.452 |  | 250.3561 | 83.452
|  | Minimum Rebate Paid | 150 |  |  |  | This should be ignored by Salesforce
For additional support:
|  | Business HVAC Program Support: | Gary.R.Reynolds@fpl.com
Mike.Catarzi@fpl.com
|  | Busines HVAC Technical Support: | Chi.Lui@fpl.com
Abel.Alonso@fpl.com
EER to SEER
| Rebate | BES | Code |  |  |  | >=760 Mbtuh |  |  | 240 =< Mbtuh < 760 MBtuh |  |  | 135 =< Mbtuh < 240 MBtuh |  |  | 65 =< Mbtuh < 135 Mbtuh |  |  | < 65 MBtuh |  | 82%
| Paym $/kw | Factor | 7% |  |  |  | EER Basis |  | Qualify | EER Basis |  | Qualify | EER Basis |  | Qualify | EER Basis |  | Qualify | SEER Basis |  | Qualify
| 165 | 88.9% | EER => |  |  |  | 9.7 |  | 9.979 | 10 |  | 10.5 | 11 |  | 11.47 | 11.2 |  | 11.984 | 13.4 |  | 14.038
FPL Rebates DX
Must Meet Efficiency Standards ASHRAE 90.1
| 1 | 2 | 3 |  |  |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Dx Unitary
| Cap Tons | [5 empty] | 4: Tons ≥ 63.33; 7: 20 ≤ Tons < 63.33; 10: 11.25 ≤ Tons < 20; 13: 5.42 ≤ Tons < 11.25; 16: Tons < 5.42
| Cap MBtuh | [5 empty] | 4: MBtuh ≥ 760; 7: 240 ≤ MBtuh < 760; 10: 135 ≤ MBtuh < 240; 13: 65 ≤ MBtuh < 135; 16: MBtuh < 65
| Eff | Eff | Eff |  |  |  | Rebate >63 |  | Reduction | Rebate 20 to 63 |  | Reduction | Rebate |  | Reduction | Rebate |  | Reduction | Rebate |  | Reduction
| (S)EER | KW/TON | COP |  |  |  | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh
| 10 | 1.2 | 2.9308 |  |  |  | 4: 0.61875; 5: 7.425; 6: 0.0028
| 10.5 | 1.143 | 3.0774 |  |  |  | 4: 1.3117; 5: 15.741; 6: 0.007; 7: 0.8415; 8: 10.098; 9: 0.0042
| 11 | 1.091 | 3.2239 |  |  |  | 4: 1.5202; 5: 18.2427; 6: 0.0108; 7: 1.485; 8: 17.82; 9: 0.0081
| 11.5 | 1.043 | 3.3705 |  |  |  | 1.6414 | 19.6965 | 0.0144 | 1.6027 | 19.2327 | 0.0116 | 0.71775 | 8.613 | 0.0036
| 12 | 1 | 3.517 |  |  |  | 1.8171 | 21.805 | 0.0176 | 1.76 | 21.12 | 0.0148 | 1.2293 | 14.751 | 0.0067 | 0.693 | 8.316 | 0.0053
| 12.5 | 0.96 | 3.6635 |  |  |  | 2.0175 | 24.2105 | 0.0205 | 1.8162 | 21.795 | 0.0178 | 1.3817 | 16.5805 | 0.0097 | 0.8712 | 10.4544 | 0.0083
| 13 | 0.923 | 3.8101 |  |  |  | 2.1879 | 26.2548 | 0.0233 | 1.8777 | 22.5324 | 0.0205 | 1.4784 | 17.7412 | 0.0124 | 1.3167 | 15.8004 | 0.011
| 13.5 | 0.889 | 3.9566 |  |  |  | 2.6004 | 31.2048 | 0.0258 | 2.2968 | 27.5616 | 0.023 | 1.6962 | 20.3544 | 0.015 | 1.7358 | 20.8296 | 0.0135 | 1.254 | 15.048 | 0.0006
| 14 | 0.857 | 4.1032 |  |  |  | 2.9964 | 35.9568 | 0.0282 | 2.6862 | 32.2344 | 0.0254 | 2.0823 | 24.9876 | 0.0173 | 2.1252 | 25.5024 | 0.0159 | 1.65 | 19.8 | 0.0035
| 14.5 | 0.828 | 4.2497 |  |  |  | 3.3429 | 40.1148 | 0.0303 | 3.0459 | 36.5508 | 0.0276 | 2.4387 | 29.2644 | 0.0195 | 2.4783 | 29.7396 | 0.018 | 1.9965 | 23.958 | 0.0061
| 15 | 0.8 | 4.3962 |  |  |  | 3.6894 | 44.2728 | 0.0324 | 3.3825 | 40.59 | 0.0296 | 2.7852 | 33.4224 | 0.0216 | 2.8215 | 33.858 | 0.0201 | 2.343 | 28.116 | 0.0086
| 15.5 | 0.774 | 4.5428 |  |  |  | 4.0029 | 48.0348 | 0.0343 | 3.7059 | 44.4708 | 0.0316 | 3.0987 | 37.1844 | 0.0235 | 3.1383 | 37.6596 | 0.022 | 2.6565 | 31.878 | 0.011
| 16 | 0.75 | 7 |  |  |  | 4.2999 | 51.5988 | 0.0361 | 3.993 | 47.916 | 0.0333 | 3.3957 | 40.7484 | 0.0253 | 3.432 | 41.184 | 0.0238 | 2.9535 | 35.442 | 0.0132
| 16.5 | 0.727 | 4.8359 |  |  |  | 4.5804 | 54.9648 | 0.0378 | 4.2768 | 51.3216 | 0.035 | 3.6762 | 44.1144 | 0.027 | 3.7158 | 44.5896 | 0.0255 | 3.234 | 38.808 | 0.0152
| 17 | 0.706 | 4.9824 |  |  |  | 4.8444 | 58.1328 | 0.0394 | 4.5342 | 54.4104 | 0.0366 | 3.9303 | 47.1636 | 0.0285 | 3.9732 | 47.6784 | 0.0271 | 3.498 | 41.976 | 0.0171
| 17.5 | 0.686 | 5.129 |  |  |  | 5.0886 | 61.0632 | 0.0408 | 4.7817 | 57.3804 | 0.0381 | 4.1778 | 50.1336 | 0.03 | 4.2207 | 50.6484 | 0.0286 | 3.7455 | 44.946 | 0.0189
| 18 | 0.667 | 5.2755 |  |  |  | 5.3196 | 63.8352 | 0.0422 | 5.0127 | 60.1524 | 0.0395 | 4.4088 | 52.9056 | 0.0314 | 4.4517 | 53.4204 | 0.03 | 3.9765 | 47.718 | 0.0207
| 18.5 | 0.649 | 5.422 |  |  |  | 5.5374 | 66.4488 | 0.0436 | 5.2272 | 62.7264 | 0.0408 | 4.6233 | 55.4796 | 0.0327 | 4.6662 | 55.9944 | 0.0313 | 4.191 | 50.292 | 0.0223
| 19 | 0.632 | 5.5686 |  |  |  | 5.7486 | 68.9832 | 0.0448 | 5.4417 | 65.3004 | 0.0421 | 4.8378 | 58.0536 | 0.034 | 4.8807 | 58.5684 | 0.0326 | 4.4055 | 52.866 | 0.0238
| 19.5 | 0.615 | 5.7151 |  |  |  | 5.9499 | 71.3988 | 0.0461 | 5.643 | 67.716 | 0.0433 | 5.0457 | 60.5484 | 0.0353 | 5.082 | 60.984 | 0.0338 | 4.6035 | 55.242 | 0.0253
| 20 | 0.6 | 5.8617 |  |  |  | 6.1314 | 73.5768 | 0.0472 | 5.8335 | 70.002 | 0.0445 | 5.2272 | 62.7264 | 0.0364 | 5.2668 | 63.2016 | 0.0349 | 4.785 | 57.42 | 0.0267
[7 empty] | MBtuh ≥ 760 |  |  | 240 ≤ MBtuh < 760 |  |  | 135 ≤ MBtuh < 240 |  |  | 65 ≤ MBtuh < 135 |  |  | MBtuh < 65
kW Lookup | [6 empty] | 4: #REF!; 7: #REF!; 10: #REF!; 13: #REF!; 16: #REF!
Incentive Lookup | [6 empty] | 4: #REF!; 7: #REF!; 10: #REF!; 13: #REF!; 16: #REF!
|  | DX Qualify | #REF!
|  | kW @ Meter | #REF!
Note on D3: Lui, Chi: Added factor, new effiiency must be better by 7%
Note on G6: Lui, Chi: Added IEER Baseline
Note on D16: Lui, Chi: Updated SEER2 to SEER factor; =13/13.4
Note on D17: Lui, Chi: Do not need values
Note on V58: LSN0HTR: SEER to EER Factor provided by AHRI DATA BASE
Note on J60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.4 to accomodate the 10.0 value in the table
Note on M60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced by 0.3 to accomodate the 10.5 value in the table
Note on P60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.3 to accomodate the 11.5 value in the table
Note on V60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.3 to accomodate the 14.0 value in the table
Note on V90: LSN0HTR: kW /ton Reduction =[(12/Base SEER*.82) -(New (kW/Ton)/.82))*BES Impact Factor]*1 ton/12MBtuh

## ASHRAE Std 90.1
Table 6.8.1-1 Electrically Operated Unitary Air Conditioners and Condensing Units - Minimum Efficiency Requirements
Air Conditioners, Air-Cooled
Water Cooled
Size Category | Heating Type | SEER | SEER2 | EER | IEER | Factor |  |  |  | EER
< 65 Mbtuh | All | 13 | 13.4 |  |  | 1.047 | (given) |  |  | 12.1 | 1.0744
≥ 65 Mbtuh and < 135 Mbtuh | Electric Resistence or none |  |  | 11.2 | 14.8 | 1.3214 |  |  |  | 12.1 | 0.92562
≥ 65 Mbtuh and < 135 Mbtuh | All Other |  |  | 11 | 14.6 | 1.3273 |  |  |  | 11.9 | 0.92437
≥ 135 Mbtuh and < 240 Mbtuh | Electric Resistence or none |  |  | 11 | 14.2 | 1.2909 |  |  |  | 12.5 | 0.88
≥ 135 Mbtuh and < 240 Mbtuh | All Other |  |  | 10.8 | 14 | 1.2963 |  | 1.3082 |  | 12.3 | 0.87805
≥ 240 Mbtuh and < 760 Mbtuh | Electric Resistence or none |  |  | 10 | 13.2 | 1.32 |  |  |  | 12.4 | 0.80645
≥ 240 Mbtuh and < 760 Mbtuh | All Other |  |  | 9.8 | 13 | 1.3265 |  |  |  | 12.2 | 0.80328
≥ 760 Mbtuh | Electric Resistence or none |  |  | 9.7 | 12.5 | 1.2887 |  |  |  | 12.2 | 0.79508
≥ 760 Mbtuh | All Other |  |  | 9.5 | 12.3 | 1.2947 |  |  |  | 12 | 0.79167
0.87543
`
Table 6.8.1-2 Electrically Operated Unitary Heat Pumps - Minimum Efficiency Requirements | [8 empty] | 1.3038
Air-Cooled (cooling mode)
Size Category | Heating Type | SEER | SEER2 | EER | IEER | Factor
< 65 Mbtuh | All | 14 | 14.3 |  |  | 1.0214 | (given)
≥ 65 Mbtuh and < 135 Mbtuh | Electric Resistence or none |  |  | 11 | 14.1 | 1.2818
≥ 65 Mbtuh and < 135 Mbtuh | All Other |  |  | 10.8 | 13.9 | 1.287
≥ 135 Mbtuh and < 240 Mbtuh | Electric Resistence or none |  |  | 10.3 | 13.5 | 1.3107
≥ 135 Mbtuh and < 240 Mbtuh | All Other |  |  | 10.4 | 13.3 | 1.2788 |  | 1.2995
≥ 240 Mbtuh and < 760 Mbtuh | Electric Resistence or none |  |  | 9.5 | 12.5 | 1.3158
≥ 240 Mbtuh and < 760 Mbtuh | All Other |  |  | 9.3 | 12.3 | 1.3226
10
Another option to consider... Convert to EER first, then input EER only in formula
Step #1:
|  | SEER2 |  | = |  | EERnew
|  | IEER |  | = |  | EERnew
SEER | SEER2
12 | 12.6 | 1.05
13 | 13.6 | 1.0462
14 | 14.7 | 1.05
15 | 15.7 | 1.0467
16 | 16.8 | 1.05
17 | 17.8 | 1.0471
18 | 18.8 | 1.0444
19 | 19.9 | 1.0474
20 | 20.9 | 1.045
21 | 22 | 1.0476
22 | 23 | 1.0455
23 | 24.1 | 1.0478
24 | 25.1 | 1.0458
25 | 26.2 | 1.048
26 | 27.2 | 1.0462
27 | 28.3 | 1.0481
28 | 29.3 | 1.0464
29 | 30.4 | 1.0483
30 | 31.3 | 1.0433
1.047
https://nee.sharepoint.com/:x:/r/teams/EXT_EXTDSMSProjectTeamsChannel/_layouts/15/Doc.aspx?sourcedoc=%7BA7941B36-3EC4-4E18-B673-C26F641D505C%7D&file=Business%20HVAC%20DX%20Calculation%20R4-07312023.xlsx&action=default&mobileredirect=true