## ERV
Energy Recovery Ventilation (ERV) Calculation
Required Inputs: Thermal Effectiveness, Pressure Drop, SCFM
Job Specific Inputs |  | ERV
Description | Code | Value
AHRI's Net Total Cooling Thermal Effectiveness Rating | Unit_Cooling_NTER | 75.2% | Minimum Qualification must be 50% or greater
AHRI Pressure Drop ERV Unit (Inches) | Unit_Pressure Drop | 1.5
Airflow Rating (min of outside air or exhaust) scfm | Unit_Airflow_Rating | 2600
Number of Units |  | 5
Program Level Inputs
Cooling Rebate
Outside Air Flow | Out_Air_Flow | 1 |  | scfm => | Out_lbs_per_hr | 4.5 | lb/hr @ | 0.075 | Lb/Cu Ft
Efficiency Basis | ERV_EER | 11.8 |  | EER | Basis_kWperTon | 1.0169 | kw/ton
Outside Air | Out_Cool_Enthalpy | 41.396 |  | Btu/lb @ | Outside Conditions Temperatures |  | DB | 95 F | WB | 78 F
Exhaust Air | Exh_Cool_Enthalpy | 28.485 |  | Btu/lb @ | Indoor Conditions Temperatures |  | DB | 75 F | WB | 63 F
Fan Eff | Fan_Eff | 60% |  | Eff
Motor Eff | Motor_Eff | 85.5% |  | Eff
BES Impact Factor | BES | 100% | [8 empty] | Air Horse Power
Filter Pres Drop | Filter_PD | 0.6 |  | inch | [6 empty] | PAHP = q* dpinWG*SG / 6356
Aux Power | Aux_Power | 0.05 |  | kW/1000 cfm | [6 empty] | where
Minimum Qualified Thermal Effectiveness | MIN_NTER | 50% | [9 empty] | PAHP = Air Horse Power (hp)
FPL Rebate ===> | ERV_Inc | 940 |  | $/kW | [7 empty] | q = air flow (cfm)
Summer kW Factor | ERV_SkW | 1 | [9 empty] | SG = Specific Gravity Air (= 1.0)
Winter kW Factor | ERV_WkW | 2.96 | [9 empty] | dpinWG = total pressure (in. W.G)
kWh Factor | ERV_kWh | 1517
CALCULATIONS
Meets minimum NTER qualifications | YES
AHRI's Net Total Cooling Thermal Effectiveness Rating | Calc_NTER | 0.752
Cooling Watts per CFM | = | Outside Air Removed (lb/hr) * AHRI Net Thermal Effect * (Outside Enthalpy (BTU/lb) - Exhaust Enthalpy (Btu/lb))/12,000 (btu/ton) * Base Efficiency (kW/ton) - (Outside Air Flow (scfm) * [(AHRI Press Drop (inch) + Filter Pressure Drop (inch))/(6356 * Fan Eff * Motor Eff))*.746 kW/HP*2 motors - Aux Power (kW/1000 cfm)/1000) * (BES)*1000
| = | 2.6917
Total Cooling kW at Meter | = | 6.9984
Results |  |  | Multiple Units
Summer kW |  | 6.9984 | 34.992
Winter kW |  | 20.7153 | 103.5763
kWh |  | 10616.5756 | 53082.878
Incentive |  | 6578.4977 | 32892.4887
DNQ = DOES NOT QUALIFY
For additional support:
Business HVAC Program Support: |  | Mike.Catarzi@fpl.com
Busines HVAC Technical Support: |  | Chi.Lui@fpl.com
Abel.Alonso@fpl.com
Note on H15: Lui, Chi: Refer to Janese Table column "I", this is amount of moisture removed, value remain the same for all
Note on C16: Changed from 11.2 to 11.8: Based on 10 Tons DX minimum efficiency per ASHRAE 90.1 - 2019
Note on C19: Lui, Chi: 0.50 changed to 0.60 based on ASHRAE requirement of FEI<=1.0 equate Fan Eff of 0.60 (AMCA 208-2018)
Note on C20: Lui, Chi: Changed from 84% to 85.5% based on EISA 2007
Note on C22: Lui, Chi: 0.30 changed to 0.60 inch pressure drop based on ASHRAE min filter MERV-8

## ERV Cool & Heat (hidden)
Energy Recovery Ventilator Rebate Table - HVAC Systems
$ Per Cfm Air Flow |  | Wattage Reduction per Cfm
Based on AHRI Standard 1060
AHRI Net Thermal Effectiveness Rating ===>
| 52.5% |  | 57.5% |  | 62.5% |  | 67.5% |  | 72.5% |  | 77.5% |  | 82.5%
| 50% to 54% | Savings | 55% to 59% | Savings | 60% to 64% | Savings | 65% to 69% | Savings | 70% to 74% | Savings | 75% to 79% | Savings | 80% or more | Savings
AHRI PD Inches | $ per cfm | watts per cfm | $ per cfm | watts per cfm | $ per cfm | watts per cfm | $ per cfm | watts per cfm | $ per cfm | watts per cfm | $ per cfm | watts per cfm | $ per cfm | watts per cfm
0.1 | 2.08 | 2.2146 | 2.31 | 2.4608 | 2.54 | 2.707 | 2.78 | 2.9532 | 3.01 | 3.1994 | 3.24 | 3.4456 | 3.47 | 3.6917
0.2 | 2.04 | 2.1689 | 2.27 | 2.4151 | 2.5 | 2.6612 | 2.73 | 2.9074 | 2.96 | 3.1536 | 3.2 | 3.3998 | 3.43 | 3.646
0.3 | 2 | 2.1231 | 2.23 | 2.3693 | 2.46 | 2.6155 | 2.69 | 2.8617 | 2.92 | 3.1079 | 3.15 | 3.354 | 3.38 | 3.6002
0.4 | 1.95 | 2.0774 | 2.18 | 2.3235 | 2.42 | 2.5697 | 2.65 | 2.8159 | 2.88 | 3.0621 | 3.11 | 3.3083 | 3.34 | 3.5545
0.5 | 1.91 | 2.0316 | 2.14 | 2.2778 | 2.37 | 2.524 | 2.6 | 2.7701 | 2.84 | 3.0163 | 3.07 | 3.2625 | 3.3 | 3.5087
0.6 | 1.87 | 1.9858 | 2.1 | 2.232 | 2.33 | 2.4782 | 2.56 | 2.7244 | 2.79 | 2.9706 | 3.02 | 3.2168 | 3.26 | 3.4629
0.7 | 1.82 | 1.9401 | 2.06 | 2.1863 | 2.29 | 2.4324 | 2.52 | 2.6786 | 2.75 | 2.9248 | 2.98 | 3.171 | 3.21 | 3.4172
0.8 | 1.78 | 1.8943 | 2.01 | 2.1405 | 2.24 | 2.3867 | 2.47 | 2.6329 | 2.71 | 2.8791 | 2.94 | 3.1252 | 3.17 | 3.3714
0.9 | 1.74 | 1.8486 | 1.97 | 2.0947 | 2.2 | 2.3409 | 2.43 | 2.5871 | 2.66 | 2.8333 | 2.89 | 3.0795 | 3.13 | 3.3257
1 | 1.69 | 1.8028 | 1.93 | 2.049 | 2.16 | 2.2952 | 2.39 | 2.5414 | 2.62 | 2.7875 | 2.85 | 3.0337 | 3.08 | 3.2799
1.1 | 1.65 | 1.757 | 1.88 | 2.0032 | 2.11 | 2.2494 | 2.35 | 2.4956 | 2.58 | 2.7418 | 2.81 | 2.988 | 3.04 | 3.2342
1.2 | 1.61 | 1.7113 | 1.84 | 1.9575 | 2.07 | 2.2037 | 2.3 | 2.4498 | 2.53 | 2.696 | 2.77 | 2.9422 | 3 | 3.1884
1.3 | 1.57 | 1.6655 | 1.8 | 1.9117 | 2.03 | 2.1579 | 2.26 | 2.4041 | 2.49 | 2.6503 | 2.72 | 2.8965 | 2.95 | 3.1426
1.4 | 1.52 | 1.6198 | 1.75 | 1.866 | 1.99 | 2.1121 | 2.22 | 2.3583 | 2.45 | 2.6045 | 2.68 | 2.8507 | 2.91 | 3.0969
1.5 | 1.48 | 1.574 | 1.71 | 1.8202 | 1.94 | 2.0664 | 2.17 | 2.3126 | 2.41 | 2.5588 | 2.64 | 2.8049 | 2.87 | 3.0511
1.6 | 1.44 | 1.5283 | 1.67 | 1.7744 | 1.9 | 2.0206 | 2.13 | 2.2668 | 2.36 | 2.513 | 2.59 | 2.7592 | 2.83 | 3.0054
1.7 | 1.39 | 1.4825 | 1.62 | 1.7287 | 1.86 | 1.9749 | 2.09 | 2.2211 | 2.32 | 2.4672 | 2.55 | 2.7134 | 2.78 | 2.9596
1.8 | 1.35 | 1.4367 | 1.58 | 1.6829 | 1.81 | 1.9291 | 2.04 | 2.1753 | 2.28 | 2.4215 | 2.51 | 2.6677 | 2.74 | 2.9138
1.9 | 1.31 | 1.391 | 1.54 | 1.6372 | 1.77 | 1.8834 | 2 | 2.1295 | 2.23 | 2.3757 | 2.46 | 2.6219 | 2.7 | 2.8681
2 | 1.26 | 1.3452 | 1.5 | 1.5914 | 1.73 | 1.8376 | 1.96 | 2.0838 | 2.19 | 2.33 | 2.42 | 2.5761 | 2.65 | 2.8223
Heating Rebates Applies Only to Electrically Heated Facilities
Elect Strip | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Example DX/ERV Rebate Calculations
Airflow Rating (min of outside air or exhaust) |  |  |  |  | 1000 | scfm
ARI's Pressure Drop ERV Unit |  |  |  |  | 1
ARI's Net Total Cooling Thermal Effectiveness Rating |  |  |  |  | 70%
ERV Cooling Rebate per 940 scfm |  |  |  |  | 2.62 | / cfm
ARI's Net Total Heating Thermal Effectiveness Rating |  |  |  |  | 74%
Rebate = | 2.62 | per cfm X | 940 | cfm => | 2462.8 | Total Rebate
Summer KW = |  |  |  |  | 2.7875 | KW
Assumptions |  | Cooling Rebate
FPL Rebate ===> |  | 940 | $/kW | 100% | BES Impact Factor
Outside Air Flow |  | 1 | scfm => | 4.5 | lb/hr @ | 0.075 | Lb/Cu Ft
Efficiency Basis |  | 11.8 | EER | 1.0169 | kw/ton
Outside Air |  | 41.396 | Btu/lb @ | 95 F | DB | 78 F | WB
Exhaust Air |  | 28.485 | Btu/lb @ | 75 F | DB | 63 F | WB
Fan Eff |  | 60% | Eff | Filter Pres Drop |  | 0.6 | inch
Motor Eff |  | 85.5% | Eff | Aux Power |  | 0.05 | kW/1000 cfm
Average kW Reduction |  | 2.5414 | kW | Pressure Drop Range Average 0.70 => 1.30
Average $ per CFM |  | 2.3889 | per CFM
Rebate |  | 2.3 | per CFM
Inputs: | ARI's Pressure Drop ERV Unit | Inch
| ARI's Net Total Cooling Thermal Effectiveness Rating | %
| AHRI's Exhaust airflow (CFM) | CFM
| AHRI's Outside airflow (CFM) | CFM
Conditions: | Calculation for rebate: use lower CFM value provided bewtween exhaust and outside airflow
Outputs: | Rebate dollar amount
| KW reduction at the meter (summer) |  | 2.7875 | Based on sample calculation above
| KW reduction at the meter (winter) = 2.96 X Summer KW reduction at meter |  | 8.2511
| KWh = 1517.0 for every summer kW reduction at the meter |  | 4228.7039
Notes
1. The AHRI Net Total Thermal Effectiveness for the cooling condition must be 50% or greater to qualify for ERV Rebate
2. The airflow capacity for Rebate calculations shall be the actual exhaust air flow or outside air flow, whichever is least, as specified in the ERV equipment specifications.
3. AHRI‘s100% Nominal Airflow capacity will be used for the airflow Rebate calculations if actual air flow exceeds AHRI’s listed 100% Nominal Airflow.
4. The Net Total Thermal Effectiveness from AHRI’s 75% Airflow Conditions shall be used if ERV equipment actual outside or exhaust air flow specifications are 75% or less of AHRI Nominal Airflow capacity.
5. A copy of air flow design submittal for the ERV must be received by FPL prior to Rebate payment processing.
6. Rebate Program does not apply to new construction projects that required ERV by code
Note on G49: Lui, Chi: Refer to Janese Table column "I", this is amount of moisture removed, value remain the same for all
Note on E50: Changed from 11.2 to 11.8: Based on 10 Tons DX minimum efficiency per ASHRAE 90.1 - 2019
Note on E53: Lui, Chi: 0.50 changed to 0.60 based on ASHRAE requirement of FEI<=1.0 equate Fan Eff of 0.60 (AMCA 208-2018)
Note on I53: Lui, Chi: 0.30 changed to 0.60 inch pressure drop based on ASHRAE min filter MERV-8
Note on E54: Lui, Chi: Changed from 84% to 85.5% based on EISA 2007