## KDCV
Kithchen Demand Control Ventilation (KDCV) Calculation
Required Input: Airflow of Exhaust Hood (cfm)
Job Specific Inputs |  | KDCV
Description | Code | Value
Airflow of Exhaust Hood (cfm) | Kitchen_Exh_CFM_New | 2900
Number of like Units Installed | Kitchen_Exh_CFM_New | 1
Program Level Inputs
Energy Savings per CFM (kW/1000cfm) | KDCV_kw_savings_per_cfm | 0.56
Base Energy Factor | KDCV_BEF | 1
FPL Rebate per kW | KDCV_Inc | 1515
Summer kW Factor | KDCV_SkW | 1
Winter kW Factor | KDCV_WkW | 5.63
kWh Factor | KDCV__kWh | 2066
Calculations
Kitchen Exhaust kW at the Meter | = | Energy Savings per CFM (kW/cfm) * Airflow Exhaust Hood (cfm)/1000
| KDCV_kW_at_Meter | 1.624
Results |  |  | If multiple units
Summer kW |  | 1.624 | 1.624
Winter kW |  | 9.1431 | 9.1431
kWh |  | 3355.184 | 3355.184
Incentive |  | 2460.36 | 2460.36
DNQ = DOES NOT QUALIFY
For additional support:
Business HVAC Program Support: |  | Mike.Catarzi@fpl.com
Busines HVAC Technical Support: |  | Chi.Lui@fpl.com
Abel.Alonso@fpl.com

## Kitchen Demand Control Vent (hidden)
Kitchen Demand Control Ventilation Rebate Table
0.848 |  | 1515 |  | 0.56 | 100% | 0.848 |  | 1515 |  | 0.56 | 100%
per CFM |  | per kW |  | kW/1000cfm | Impact | per CFM |  | per kW |  | kW/1000cfm | Impact | Note
Hood Exhaust Air |  |  | Cap Used | Rebate Dollars | Reduced | Hood Exhaust Air |  |  | Cap Used | Rebate Dollars | Reduced | Off Factor Adjusts for Difference Between
|  |  | CFM |  | kw |  |  |  | CFM |  | kw | Mainframe Rounding vs Spreadsheets | First Column | Revised
0 | < CFM ≤ | 300 | 150 | 127.26 | 0.084 | 6000 | < CFM ≤ | 7750 | 6875 | 5833 | 3.85 |  | 1515 | 1515.0649
300 | < CFM ≤ | 600 | 450 | 381.78 | 0.252 | 7750 | < CFM ≤ | 9500 | 8625 | 7317 | 4.83 |  | 1515 | 1514.9068
600 | < CFM ≤ | 900 | 750 | 636.3 | 0.42 | 9500 | < CFM ≤ | 11250 | 10375 | 8802 | 5.81 |  | 1515 | 1514.9742 | Cost Effectiveness Testing Inputs
900 | < CFM ≤ | 1200 | 1050 | 890.82 | 0.588 | 11250 | < CFM ≤ | 13000 | 12125 | 10287 | 6.79 |  | 1515 | 1515.0221 | Intellihood Exhaust Fan Controller for Commercial Kitchens
1200 | < CFM ≤ | 1500 | 1350 | 1145.34 | 0.756 | 13000 | < CFM ≤ | 14750 | 13875 | 11772 | 7.77 |  | 1515 | 1515.0579 | Trane CDQ DX HVAC with Cromer Cycle Desiccant Wheel
1500 | < CFM ≤ | 1800 | 1650 | 1399.86 | 0.924 | 14750 | < CFM ≤ | 16500 | 15625 | 13256 | 8.75 |  | 1515 | 1514.9714
1800 | < CFM ≤ | 2100 | 1950 | 1654.38 | 1.092 | 16500 | < CFM ≤ | 18250 | 17375 | 14741 | 9.73 |  | 1515 | 1515.0051 | cost effectiveness inputs for smart kitchen exhaust hood controllers:
2100 | < CFM ≤ | 2400 | 2250 | 1908.9 | 1.26 | 18250 | < CFM ≤ | 20000 | 19125 | 16226 | 10.71 |  | 1515 | 1515.0327 | Impacts to peak demand (kW) and annual energy (kWh)
2400 | < CFM ≤ | 2700 | 2550 | 2163.42 | 1.428 | 20000 | < CFM ≤ | 21750 | 20875 | 17710 | 11.69 |  | 1515 | 1514.9701 |  |  | reduction | reduction | savings | ratio | participant | participant | cost effective | payback in years | proposed | payback in years | Total Rebate | Total Rebate | cost eff | cost eff | Sum Exhaust
2700 | < CFM ≤ | 3000 | 2850 | 2417.94 | 1.596 | 21750 | < CFM ≤ | 23500 | 22625 | 19195 | 12.67 |  | 1515 | 1514.9961 | code |  | summer peak kW | winter peak kW | annual kWh | kWh/summer kW | incremental cost | incremental $/summer kW | max Rebate $/kW | at max Rebate | Rebate $/kW | at proposed $/kW | at maximum $/kW | at proposed $/kW | RIM test | Participant test | Flow (cfm)
3000 | < CFM ≤ | 3300 | 3150 | 2672.46 | 1.764 | 23500 | < CFM ≤ | 25250 | 24375 | 20680 | 13.65 |  | 1515 | 1515.0183 | KXSU | Supermarket | 4.3 | 26.1 | 39300 | 9139.5349 | 8389 | 1950.9302 | 200 | 2.01 | 200 | 2.01 | 860 | 860 | pass | pass | 6445
3300 | < CFM ≤ | 3600 | 3450 | 2926.98 | 1.932 | 25250 | < CFM ≤ | 27000 | 26125 | 22164 | 14.63 |  | 1515 | 1514.9692 | KXRE | Restaurant | 3.6 | 1.4 | 33000 | 9166.6667 | 16028 | 4452.2222 | 1000 | 3.9 | 1000 | 3.9 | 3600 | 3600 | pass | pass | 10226
3600 | < CFM ≤ | 3900 | 3750 | 3181.5 | 2.1 | 27000 | < CFM ≤ | 28750 | 27875 | 23649 | 15.61 |  | 1515 | 1514.9904 | KXFC | Fast Food cond ma | 3.5 | 0 | 13900 | 3971.4286 | 8371 | 2391.7143 | 1500 | 2.06 | 1000 | 3.09 | 5250 | 3500 | pass | pass | 2815
3900 | < CFM ≤ | 4200 | 4050 | 3436.02 | 2.268 | 28750 | < CFM ≤ | 30500 | 29625 | 25134 | 16.59 |  | 1515 | 1515.009 | KXFU | Fast Food uncond ma | 1 | 0 | 4900 | 4900 | 8371 | 8371 | 1500 | 13.39 | 1000 | 20.085 | 1500 | 1000 | pass | fail | 2815
4200 | < CFM ≤ | 4500 | 4350 | 3690.54 | 2.436 | 30500 | < CFM ≤ | 32250 | 31375 | 26619 | 17.57 |  | 1515 | 1515.0256 | KXHC | Average | 3.1 | 6.875 | 22775 | 7346.7742 | 10289.75 | 3319.2742 | 1850 | 0 | 1850 | 2.02 | 10289.75 | 5735 | pass | pass
4500 | < CFM ≤ | 4800 | 4650 | 3945.06 | 2.604 | 32250 | < CFM ≤ | 34000 | 33125 | 28103 | 18.55 |  | 1515 | 1514.9865 |  | Sum | 12.4 | [10 empty] | 8960 | 722.5806 | /kw | 22301
4800 | < CFM ≤ | 5100 | 4950 | 4199.58 | 2.772 | 34000 | < CFM ≤ | 35750 | 34875 | 29588 | 19.53 |  | 1515 | 1515.0026 | [14 empty] | 600 | /kw rounded down to DCV Rebate
5100 | < CFM ≤ | 5400 | 5250 | 4454.1 | 2.94 | 35750 | < CFM ≤ | 37500 | 36625 | 31073 | 20.51 |  | 1515 | 1515.0171 | [14 empty] | 0.55603 | kW/1000 cfm summer reduction
5400 | < CFM ≤ | 5700 | 5550 | 4708.62 | 3.108 | 37500 | < CFM ≤ | 39250 | 38375 | 32557 | 21.49 |  | 1515 | 1514.9837
5700 | < CFM ≤ | 6000 | 5850 | 4963.14 | 3.276 | 39250 | < CFM ≤ | 41000 | 40125 | 34042 | 22.47 |  | 1515 | 1514.9978
For kitchen DCV a copy of the hood manufacturer specifications listing airflow capacities of the
exhaust and make-up air fans must be submitted. When not available a copy of the Test and Balance
Report, showing both exhaust and make-up airflows for the fans can be substituted for the hood | [14 empty] | Summary of fan power rating, flow rate and power measured during max. speed.
manufacturer specifications. | [14 empty] | Some motor model numbers were not looked up since it required turning off equipment that was needed to be left on at time of visit. Other cases involved motor plate info that was no longer readable due to wear. Some irregularities were noticed in the wiring for three of the motors.
Fan Flow Rate (cubic feet per minute) and
Power Measured (Watts) at full power (100% of variable speed drive).
[15 empty] | Merritt Island Publix |  | EF2 deep fryer | SF1 make-up | EF3 rotisserie
[16 empty] | Motor description | Marathon 1725 rpm, rated 3.4 fla@208v | * Dayton Watttrimmer 1725 rpm, 1.1 amp@230v | * Dayton Watttrimmer 1725 rpm, 2.3 amp @208?v
[16 empty] | Motor HP | 1 | 2007-01-03 | 2007-03-04
[16 empty] | FLOW | 4115 | 1378 | 2330
[16 empty] | POWER | 1305 | 656 | 335
[16 empty] | Rooftop EQUIPT.mod.# | CUBE-180-10-6
[15 empty] | Greenheck | RSF-90-3-X
[15 empty] | Greenheck | CUBE-141-7-6
Greenheck
[15 empty] | Miami Publix | Motor description | NA | NA | NA
[16 empty] | Motor HP | NA | NA | NA
[16 empty] | FLOW | 2952 | 1628 | 2135
[16 empty] | POWER | 815 | 434 | 584
[16 empty] | Rooftop EQUIPT.mod.# | CUBE-180-10-6
[15 empty] | Greenheck | RSF-90-3-X
[15 empty] | Greenheck | CUBE-141-7-6
Greenheck
[15 empty] | Olive Garden |  | EF1 | SF1 | EF2 | SF2
[16 empty] | Motor description | NA | * Baldor 1725rpm,3.8a @208v | NA | Baldor 1725rpm, 3.3a @208v
[16 empty] | Motor HP | NA | 1 | NA | 2007-03-04
[16 empty] | FLOW | 5788 | 1533 | 4438 | 1497
[16 empty] | POWER | 1462 | 301 | 1137 | 248
[15 empty] | Wendy's |  | EF1 | EF2 | MA unit
[16 empty] | Motor HP | NA | NA | NA
[16 empty] | FLOW | 1760 | 1055 | 3411
[16 empty] | POWER | 294 | 211 | 1000
[16 empty] | Rooftop EQUIPT.mod.# | FX13BHFT
[15 empty] | Penn Ventilator Co. | FX13BHFT Penn Ventilator Co. | NJ-3/DX-C12.5 Airwise
* Only 2 lines out of three were found to carry any voltage or current on these three phase motors.
Note on G7: Alonso, Abel: BES Factor
Note on N7: Alonso, Abel: BES Factor